## Table 1 A & B
Table 1A. Data Summary Part A
[6 empty] | Q | Wfuel | MCave | Qin | Qout
Category | Run No. | Load % Capacity | Target Load | Actual Load | Actual Load | Test Duration | Wood Weight as-fired | Wood Moisture | Heat Input | Heat Output
|  |  | Btu/hr | Btu/hr | % of Max | hrs | lb | % DB | Btu | Btu
I |  | <15% of Max | 34800 | 31983.634 | 13.79% | 26.1333 | 161.11 | 23.33 | 1123419.8537 | 835838.9693 | 0%
II |  | 16-24% of Max | 55680 | 52530.2705 | 22.64% | 15.5667 | 152.94 | 23.25 | 1067186.4458 | 817721.2101 | 0%
III |  | 25-50% of max | 116000 | 113877.5538 | 49.09% | 7.6667 | 156.08 | 21.58 | 1104048.24 | 873061.2458 | 0%
IV |  | Max capacity | 232000 | 214636.1626 | 92.52% | 3.7833 | 156.26 | 23.11 | 1091555.9494 | 812040.1486 | 0%
Table 1B. Data Summary Part B
|  |  | T2 Min | ET | E | E | Eg/hr | Eg/kg | hdel | hSLM
Category | Run No. | Load % Capacity | Min Return Water Temp. | Total PM Emissions | PM Output Based | PM Output Based | PM Rate | PM Factor | Delivered Efficiency | Stack Loss Efficiency
|  |  | ºF | g | lb/mmBtu Out | g/MJ | g/hr | g/kg | % | %
I |  | <15% of Max | 149.61 | 31.35 | 0.08269 | 0.035552 | 1.1996 | 0.52894 | 74.4% | 77.7%
II |  | 16-24% of Max | 149.09 | 24.3232 | 0.065577 | 0.028213 | 1.5635 | 0.43229 | 76.62% | 78.9%
III |  | 25-50% of max | 142.8 | 16.2884 | 0.041131 | 0.017684 | 2.1246 | 0.27964 | 79.08% | 79.4%
IV |  | Max capacity | 122.91 | 19.3344 | 0.052492 | 0.022568 | 5.1104 | 0.33573 | 74.39% | 82.4%
* NOTE: The Stack Loss Efficiency for the category 1 did result in two anomalies. 1) During the long off cycles, the CO and CO2 was reading zero; therefore giving high excess air numbers. The off cycle numbers were removed from the data. 2) During the on cycles, the CO2 numbers were reading as high as 27%. This concluded that there was some electrical interference and these numbers were removed from the data.

## Hang Tag Info
Table 1C: Hang Tag Information
MANUFACTURER: | SteelTech
MODEL NUMBER: | G200
MAXIMUM OUTPUT RATING: | 232000 |  | Btu/hr
8-HOUR OUTPUT RATING: | Qout-8hr | 111315 | Btu/hr
8-HOUR AVERAGE EFFICIENCY: | havg-8hr | 79% | (Using higher heating value)
|  | 85% | (using lower heating value)
ANNUAL EFFICIENCY RATING: | havg | 76.22% | (Using higher heating value)
|  | 82.06% | (using lower heating value)
PARTICULATE EMISSIONS: | Eavg | 1.7361 | GRAMS/HR (average)
|  | 0.065678 | LBS/MILLION Btu OUTPUT

## Yr Rnd Weighted
Table 2. Year Round Use Weighting
Category | Run No. | Weighting Factor | hdel,i x Fi-HHV | hdel,i x Fi-LHV | Eg/MJ,i x Fi | Eg/kg,i x Fi | Elb/mmbtu,i x Fi | Eg/hr,i x Fi
I |  | 0.437 | 0.32513 | 0.35004 | 0.015536 | 0.23115 | 0.036135 | 0.52423
II |  | 0.238 | 0.18237 | 0.19634 | 0.0067147 | 0.10289 | 0.015607 | 0.37212
III |  | 0.275 | 0.21746 | 0.23413 | 0.0048631 | 0.076901 | 0.011311 | 0.58426
IV |  | 0.05 | 0.037196 | 0.040046 | 0.0011284 | 0.016787 | 0.0026246 | 0.25552
Totals |  | 1 | 76.22% | 82.06% | 0.028242 | 0.42772 | 0.065678 | 1.7361
*Cat II Weightings = (0.437 + .238) / 2 = 0.338