## Sheet1
|  | Project No: | G101258894 |  | Manufacturer: | SteelTech | Model: | G200 |  | Date: | 2013-09-12 |  | Tech:
Weighted Average for Outdoor Wood Fired hydronic Heating Appliances
CAT | Load % Capacity | Tgt Load (Btu/hr) | Act Load (Btu/hr) | Test Duration | WoodWt | Qin | Qout | hN | ET | E | E Output | E Input | E | E | E
|  |  |  | (Hours) | (Lb) | (Btu) | (Btu) | (%) | (g) | (g/MJ) | (lb/mmbtu) | (lb/mmbtu) | (g/hr) | (g/Kg) | (g/hr 10,000 btu)
I | <15% of max | 34800 | 31983.634 | 26.1333 | 161.11 | 1123419.8537 | 835838.9693 | 74.4% | 31.35 | 0.035552 | 0.08269 | 0.061522 | 1.1996 | 0.52894 | 0
II | 16 – 24% of max | 55680 | 52530.2705 | 15.5667 | 152.94 | 1067186.4458 | 817721.2101 | 76.62% | 24.3232 | 0.028194 | 0.065577 | 0.050248 | 1.5625 | 0.43201 | 0
III | 25 -50% of max | 116000 | 113877.5538 | 7.6667 | 156.08 | 1104048.24 | 873061.2458 | 79.08% | 16.2884 | 0.017684 | 0.041131 | 0.032526 | 2.1246 | 0.27964 | 0
IV | Max capacity | 232000 | 214636.1626 | 3.7833 | 156.26 | 1091555.9494 | 812040.1486 | 74.39% | 19.3344 | 0.022568 | 0.052492 | 0.03905 | 5.1104 | 0.33573 | 0
|  |  |  | Efficiency | Efficiency
| Average BTU/hr for 8 hr burn time |  | 111315.362 | 79% | 84.99% | Y1 | 15.57 | Test duration above 8 hours
|  |  |  | HHV | LHV | Y2 | 7.67 | Test duration just below 8 hours
[6 empty] | X1 | 52530 | Actual load (BTU/hr) for duration Y1
|  |  | If the test is ASTM put a 0, if EPA put a 1 | 1 |  | X2 | 113878 | Actual load (BTU/hr) for duration Y2
[6 empty] | Z1 | 76.6% | Efficiency for duration Y1 HHV
| Maximum output rating BTU/hr: | 232000 |  |  |  | Z2 | 79.1% | Efficiency for duration Y2 HHV
[6 empty] | Z3 | 82.5% | Efficiency for duration Y1 LHV
[6 empty] | Z4 | 85.1% | Efficiency for duration Y2 LHV
Heating Season Weighting
| Weighting |  |  |  | Input | Output
Category | Factor | h x Fi HHV | Eg/MJ,I x Fi | Eg/kg,I x F i | Elb/mmbtu x Fi | Elb/mmbtu x Fi | Eg/hr x Fi | h x Fi LHV
I | 0.175 | 0.1302 | 0.0062216 | 0.092564 | 0.010766 | 0.014471 | 0.20993 | 0.14018
II | 0.275 | 0.21072 | 0.0077535 | 0.1188 | 0.013818 | 0.018034 | 0.42969 | 0.22686
III | 0.45 | 0.35585 | 0.0079578 | 0.12584 | 0.014637 | 0.018509 | 0.95606 | 0.38312
IV | 0.1 | 0.074393 | 0.0022568 | 0.033573 | 0.003905 | 0.0052492 | 0.51104 | 0.080093
Totals | 1 | 0.77116 | 0.02419 | 0.37078 | 0.043126 | 0.056263 | 2.1067 | 0.83025
Year Round Use Weighting
| Weighting |  |  |  | Input | Output
Category | Factor | h x Fi HHV | Eg/MJ,I x Fi | Eg/kg,I x F i | Elb/mmbtu x Fi | Elb/mmbtu x Fi | Eg/hr x Fi | h x Fi LHV
I | 0.437 | 0.32513 | 0.015536 | 0.23115 | 0.026885 | 0.036135 | 0.52423 | 0.35004
II | 0.238 | 0.18237 | 0.0067103 | 0.10282 | 0.011959 | 0.015607 | 0.37188 | 0.19634
III | 0.275 | 0.21746 | 0.0048631 | 0.076901 | 0.0089446 | 0.011311 | 0.58426 | 0.23413
IV | 0.05 | 0.037196 | 0.0011284 | 0.016787 | 0.0019525 | 0.0026246 | 0.25552 | 0.040046
Totals | 1 | 0.76216 | 0.028238 | 0.42765 | 0.049741 | 0.065678 | 1.7359 | 0.82055
G:\BldProd\Hearth\Clients\SteelTech\G101258894 G200\Model G200 Data\Test #1\[Test #1.xls]Boiler particulates
Remember to use Paste special when copying to this area, values only!
Category 1 test results Paste in F51 | [5 empty] | Category 2 test results paste in L51
|  | Run Number | 2 |  |  |  |  | Run Number | 3
|  | Test Date | 2013-09-10 |  |  |  |  | Test Date | 2013-09-11
|  | Total Test Fuel Weight (lb) | 161.11 |  |  |  |  | Total Test Fuel Weight (lb) | 152.94
|  | Avg. Test Fuel Moisture (% dry) | 23.3329 |  |  |  |  | Avg. Test Fuel Moisture (% dry) | 23.2478
|  | Avg. Temp. of Water in load side (o F) | 118.5274 |  |  |  |  | Avg. Temp. of Water in load side (o F) | 119.1504
|  | Temp. Diff. in/out of Heat Exchanger (o F) | 95.7666 |  |  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 99.232
|  | Liquid Flow Rate (gal/min) | 0.68389 |  |  |  |  | Liquid Flow Rate (gal/min) | 1.0983
|  | Test Duration (min) | 1568 |  |  |  |  | Test Duration (min) | 934
|  | Burn Rate (kg/hr) | 2.2674 |  |  |  |  | Burn Rate (kg/hr) | 3.6159
|  | Emissions (g) | 31.35 |  |  |  |  | Emissions (g) | 24.3232
|  | Beginning Dry Gas Meter Reading (ft3) | 225.733 | 230.761 |  |  |  | Beginning Dry Gas Meter Reading (ft3) | 414.909 | 419.97
|  | Final Dry Gas Meter Reading (ft3) | 414.905 | 419.934 |  |  |  | Final Dry Gas Meter Reading (ft3) | 527.037 | 532.135
|  | Average Barometric Pressure (“Hg) | 29.105 |  |  |  |  | Average Barometric Pressure (“Hg) | 29.13
|  | Average Delta p (inches of water) | 0.073267 |  |  |  |  | Average Delta p (inches of water) | 0.072003
|  | Average Delta H (inches of water) | 0 |  |  |  |  | Average Delta H (inches of water) | 0
|  | Average Gas Velocity in Tunnel (feet/sec) | 16.2197 |  |  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 16.3331
|  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 764.3388 |  |  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 769.6822
|  | Water Density | 8.3151 |  |  |  |  | Water Density | 8.3228
|  | Water Specific Heat | 1.0011 | MU |  |  |  | Water Specific Heat | 1.0012 | MU
|  | Total Output | 835838.9693 | 9608.5375 |  |  |  | Total Output | 817721.2101 | 9493.7437
|  | Emissions g/MJ | 0.035552 |  |  |  |  | Emissions g/MJ | 0.028194
|  | Emissions lb/MMBtu Input | 0.061522 |  |  |  |  | Emissions lb/MMBtu Input | 0.050248
|  | Emissions lb/MMBtu Output | 0.08269 | 0.0030773 |  |  |  | Emissions lb/MMBtu Output | 0.065577 | 0.0028317
|  | Emissions g/hr/10,000 Btu Output | [5 empty] | Emissions g/hr/10,000 Btu Output
|  | Efficiency | 0.74401 | 1.4954 |  |  |  | Efficiency | 0.76624 | 1.5611
|  |  | 0.80102 | [5 empty] | 0.82495
|  | g/kg | 0.52894 |  |  |  |  | g/kg | 0.43201
|  | Input | 1123419.8537 |  |  |  |  | Input | 1067186.4458
Category 3 test results paste in F81 | [5 empty] | Category 4 test results Paste in L81
|  | Run Number | 4 |  |  |  |  | Run Number | 1
|  | Test Date | 2013-09-12 |  |  |  |  | Test Date | 2013-09-09
|  | Total Test Fuel Weight (lb) | 156.08 |  |  |  |  | Total Test Fuel Weight (lb) | 156.26
|  | Avg. Test Fuel Moisture (% dry) | 21.5787 |  |  |  |  | Avg. Test Fuel Moisture (% dry) | 23.112
|  | Avg. Temp. of Water in load side (o F) | 107.9946 |  |  |  |  | Avg. Temp. of Water in load side (o F) | 88.0271
|  | Temp. Diff. in/out of Heat Exchanger (o F) | 94.5358 |  |  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 51.9264
|  | Liquid Flow Rate (gal/min) | 2.4623 |  |  |  |  | Liquid Flow Rate (gal/min) | 8.9264
|  | Test Duration (min) | 460 |  |  |  |  | Test Duration (min) | 227
|  | Burn Rate (kg/hr) | 7.5954 |  |  |  |  | Burn Rate (kg/hr) | 15.2175
|  | Emissions (g) | 16.2884 |  |  |  |  | Emissions (g) | 19.3344
|  | Beginning Dry Gas Meter Reading (ft3) | 527.1 | 532.1 |  |  |  | Beginning Dry Gas Meter Reading (ft3) | 199.66 | 204.584
|  | Final Dry Gas Meter Reading (ft3) | 582.065 | 587.466 |  |  |  | Final Dry Gas Meter Reading (ft3) | 225.725 | 230.755
|  | Average Barometric Pressure (“Hg) | 29.1 |  |  |  |  | Average Barometric Pressure (“Hg) | 28.83
|  | Average Delta p (inches of water) | 0.072499 |  |  |  |  | Average Delta p (inches of water) | 0.070669
|  | Average Delta H (inches of water) | 0 |  |  |  |  | Average Delta H (inches of water) | 0
|  | Average Gas Velocity in Tunnel (feet/sec) | 16.3905 |  |  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 15.6595
|  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 772.3868 |  |  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 737.9385
|  | Water Density | 8.332 |  |  |  |  | Water Density | 8.3366
|  | Water Specific Heat | 1.0012 | MU |  |  |  | Water Specific Heat | 1.0012 | MU
|  | Total Output | 873061.2458 | 10264.0015 |  |  |  | Total Output | 812040.1486 | 12178.013
|  | Emissions g/MJ | 0.017684 |  |  |  |  | Emissions g/MJ | 0.022568
|  | Emissions lb/MMBtu Input | 0.032526 |  |  |  |  | Emissions lb/MMBtu Input | 0.03905
|  | Emissions lb/MMBtu Output | 0.041131 | 0.0024633 |  |  |  | Emissions lb/MMBtu Output | 0.052492 | 0.0028486
|  | Emissions g/hr/10,000 Btu Output | [5 empty] | Emissions g/hr/10,000 Btu Output
|  | Efficiency | 0.79078 | 1.6209 |  |  |  | Efficiency | 0.74393 | 1.6345
|  |  | 0.85137 | [5 empty] | 0.80093
|  | g/kg | 0.27964 |  |  |  |  | g/kg | 0.33573
|  | Input | 1104048.24 |  |  |  |  | Input | 1091555.9494